## WRO Room Only
Quantity | Description | Cost
A | WATER REVERSE OSMOSIS (RO) SYSTEM FOR 12 DIALYSIS MACHINE
1 | Haemodialysis Reverse Osmosis Water Treatment System to include: Microfiltration Cartridge Filter, 5 microns, Filmtec Membranes Flow = 10 gpm, SS316 high pressure pump (3 m3/hr, 100 m Head)pressure gauges, flow meter, Capacity = 300 L/hr.
1 set | Water Pretreatment system to include water softener, Media Filters, Activated Carbon, 1Hp Stainless Steel Transfer Pump, and UV Water Sterilizer.
1 | Piping of the Dialysis room, Electricals, Pipe & Piping fittings
3 | Black GEEPEE Water Storage Tank 1,500L
#10,000,000.00
Specification:
Water Room must have the following specification when built:
Size: 4.5m by 3.5m
Direct Power Supply from DB to:
100A Breaker
63A Breaker
63A Breaker
13A Socket
The Floor must be tiled
Floor Drain must be created
Provision of 1.5HP AC

## General Pretreatment Room
Qty | Description | Cost
B | GENERAL WATER PRE-TREATMENT SYSTEM
2 | Filtration and Backwash pump set (1 Duty / 1 Standby), complete with all valves and accessories with pressure control Capacity = 1m3/hr. Head = 35 m (PUMP Grundfos)
1 | FRP Sand Filter including Media (Sand/Gravel/Antracide) Diameter = 16", Height = 65" complete with Manual control valve, Pressure gauge, drain valve and all related accessories with FILCOM Gravel Sand.
1 | FRP Activated Carbon Filter including Media (Sand/Gravel/ Granular Activated Carbon) Diameter = 16", Height = 65" complete with Manual control valve, Pressure gauge, drain valve and all related accessories with FILCOM Gravel Sand Model # G0426 and Granual activated carbon JACOBI
1 | FRP Water Softener, including Brime system, capacity of 120,000 Grains. Diameter = 16", Height = 65" Complete with volumetric type Motorized control valve, water meter, Pressure gauge, drain valve and all related accessories
2 | RO Treated Water Booster Set ( 1 Duty/ 1 Standby) , complete with all valves and accessories with pressure control (PUMP GRUNDFOS) Capacity = 3 m3/hr. Head = 30 m
1 | Electrical and Control panel complete with all related cabling, conduiting with dry contacts (Filtration pumps, RO pumps) to be connected to BMS for monitoring
#5,000,000.00